Gas Sensor   NAP－55A

- NAP－55A

NAP-55A is a miniature & low power consumption type of NAP-2A, and is mainly used for gas detectors and leak testers. 55A is a half in height and needs a half in power consumption compared to 2A so that thinner and lighter-weight detectors can be produced. The following are the basic characteristics but it is recommended to refer to the individual user’s manual for further information. A measuring circuit for sensor evaluation is the same as NAP-2A.

Target gases and concentration

| Gases |  | Detection range |
| --- | --- | --- |
| Methane | CH4 | 0.05－5％(0.05－2％) |
| Propane | C3H8 | 0.03－2.2％(0.03－1％) |
| Iso-butane | Iso-C4H10 | 0.03－1.8％(0.03－0.8％) |
| Hydrogen | H2 | 0.05－4％(0.05－1.5％) |
| Ethanol | C2H5OH | 0.05－3.2％(0.05－1.5％) |
| Hydrocarbons | CnH2n+2 | 1-100%LEL(1-50%LEL) |

( ) is a detection range in high accuracy

Ratings

| Items | Specifications |
| --- | --- |
| Supply Voltage | DC 2.5 +/- 0.25V AC 2.5+/- 0.25V (r.m.s. 50~60Hz) |
| Current (When 2.5V is applied) | DC 150 ~ 170mA AC 150 ~ 170mA (r.m.s. 50~60Hz) |
| AmbientTemperature | In operation -10 ~ +50℃ In storage -10 -~+50℃ |
| Ambient humidity | In operation 95％RH or less In storage 99％RH or less (No dew condensation) |

Gas sensitivity characteristics

| Gases & concentration | Output voltage |
| --- | --- |
| Output in clean air | -35 ~ +35mV |
| Methane 3000ppm | 10 ~ 16mV |
| Iso-butane 1400ppm | 10 ~ 15mV |
| Hydrogen 1400ppm | 7 ~ 12mV |
| Ethanol 1400ppm | Less than 11mV |

| Gas sensitivity characteristics | Response characteristics |
| --- | --- |